| Clover Digital Sdn Bhd (Co. Reg. 201501034912) 7A Jalan PP2/1, Taman Putra Prima, 47100 Puchong, Selangor admin@cloverdigital.com.my www.cloverdigital.com.my |  |  | Engineer’s Service Report ESR No. 26/011 |
| --- | --- | --- | --- |
| Customer: TNB Engineering Corporation Sdn Bhd |  | Site Address: IJN Chiller Plant |  |
| Contact: |  | Date/Time: 21/8/2026 |  |
| Reported Fault: |  |  |  |
| STLP1 & 2 failed to run. Inverter show running but no power output to pump. |  |  |  |
| Engineer’s Report: |  |  |  |
| The existing Danfoss VLT 6000 Variable Frequency Drive (VFD) for STLP1 and STLP 2have suffered a critical failure, resulting in zero power output to the connected motor. Given the unit's age (~19 years), operation runtime (~50,000 hours), and obsolete support status, direct replacement with a modern equivalent VFD is strongly recommended over component repair. |  |  |  |
| At 50,000 operating hours, critical internal hardware—such as DC bus capacitors, power card gate drivers, IGBT modules, and internal cooling fans—has reached end-of-life. Repairing only the output stage circuit will leave other worn components intact, causing high likelihood of secondary failures shortly after startup. |  |  |  |
| The Danfoss VLT 6000 series is mature legacy hardware. Sourcing refurbished or old-stock replacement circuit boards incurs high costs and extended lead times, without restoring warranty coverage or reliable operation. |  |  |  |
| Downtime Risk & Operational Efficiency - Repair: Long lead time to source legacy components with zero guarantee of system reliability post-repair. - Replacement: Modern drives offer direct mechanical/electrical migration paths, seamless protocol integration, superior energy efficiency, full 12 month warranties, and readily available spare parts. |  |  |  |
| STLP1 STLP2 |  |  |  |
| Attended By: |  | Verified by: |  |
|  |  | Customer’s Signature |  |
| Name: SK Ding |  | Name: |  |
| Date: 21/8/2026 |  | Date: |  |